Vaporless Manufacturing

Vaporless LD-2000E, LD-2000E-S 
(for Flexible Pipelines)

AUTOMATIC MECHANICAL LINE LEAK DETECTOR

| Certification | Leak rate of 3.0 gph with PD = 100% and PFA = 0%. |
| --- | --- |
| Leak Threshold | 2.0 gph. A pipeline system should not be declared tight if the test result indicates a loss that equals or exceeds this threshold. |
| Applicability | Gasoline, diesel, aviation fuel. Other liquids may be tested after consultation with the manufacturer. |
| Specification | System tests flexible pipelines. Tests are conducted at operating pressure. |
| Pipeline Capacity | Maximum of 59.6 gallons. |
| Waiting Time | None between dispensing and testing. None between delivery and testing. |
| Test Period | Response time is 30 seconds. |
| System Features | Permanent installation on pipeline. Automatic testing of pipeline. Preset threshold. Single test to determine if pipeline is leaking. LD2000E - restricted flow to dispenser if leak is declared. LD2000ES - pump shutoff if leak is declared. |
| Calibration | System must be checked annually and, if necessary, calibrated in accordance with manufacturer's instructions. |
| Comments | Enviroflex piping with a bulk modulus* of 1,352 psi was used during evaluation. *See glossary. |

| Vaporless Manufacturing | Evaluator: Ken Wilcox Associates |
| --- | --- |
| 8700 East Long Mesa Drive | Tel: (816) 443-2494 |
| Prescott Valley, AZ 86314 | Dates of Evaluation: 12/11/92 |
| Tel: (928) 775-5191 |  |